## Estate Register
Equipment | Ref | Fault | Severity | OOH | 1 Pancras | 2 Pancras | 3 Pancras | 4 Pancras | B0 Accessway | WTS | S1 | R7 | Q1 | T2-T3 | P2 | S3 | CDY | MGS | F&C | Estate
|  | In Scope FDDs |  |  |  | 68 | 68 | 68 | 0 | 69 | 59 | 69 | 65 | 65 | 58 | 41 | 53 | 65 | 3 | 2
|  | Live FDDs |  |  |  | 22 | 14 | 13 | 0 | 14 | 10 | 14 | 10 | 12 | 11 | 0 | 7 | 10 | 0 | 0
|  | Validated FDDs |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Blocked FDDs |  |  |  | 8 | 8 | 8 | 0 | 8 | 8 | 8 | 9 | 8 | 8 | 8 | 8 | 9 | 2 | 2
|  | Live Coverage % |  |  |  | 32.35% | 20.59% | 19.12% |  | 20.29% | 16.95% | 20.29% | 15.38% | 18.46% | 18.97% | 0% | 13.21% | 15.38% | 0% | 0%
|  | Validated Coverage % |  |  |  | 0% | 0% | 0% |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Unassessed FDDs |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 6 | 6 | 6 | 4 | 33 | 12 | 6 | 142 | 143
AHU | AHU-01 | Supply Fan Failed | Critical | Y | Enabled | Enabled | Enabled | Enabled | NA | Enabled | Enabled | Enabled | Enabled | Enabled | Backlog |  | Backlog | Backlog
AHU | AHU-02 | Fan Running in Hand | Warning |  | Enabled | Enabled | Enabled | Enabled | NA | Enabled | Backlog | Enabled | Enabled | Enabled | Enabled |  | Enabled | Enabled
AHU | AHU-03 | Fan Short Cycling | Warning |  | Enabled | Enabled | Enabled | Enabled | NA | Enabled | Backlog | Enabled | Enabled | Enabled | Enabled |  | Enabled | Enabled
AHU | AHU-04 | Sensor Flatlined | Warning |  | Enabled | Enabled | Enabled | Enabled | NA | Enabled | Enabled | Enabled | Enabled | Enabled | Enabled |  | Enabled | Enabled
AHU | AHU-05 | Sensor Reading Implausible | Warning |  | Enabled | Enabled | Enabled | Enabled | NA | Enabled | Enabled | Enabled | Enabled | Enabled | Enabled |  | Enabled | Enabled
AHU | AHU-06 | Running Outside Schedule | Warning |  | NA | Enabled | NA | NA | NA | Enabled | NA | NA | NA | NA | NA | NA | NA | NA
AHU | AHU-07 | Failed to Start on Schedule | Critical |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
AHU | AHU-08 | Excessive Continuous Runtime | Alert |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
AHU | AHU-09 | Heating Valve Passing | Warning |  | Enabled | Enabled | Enabled | Enabled | NA | Enabled | Enabled | Enabled | Backlog | Enabled | Enabled |  | Backlog | Enabled
AHU | AHU-10 | Heating Valve Hunting | Alert |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
AHU | AHU-11 | Not Achieving Supply Temp (Htg) | Warning |  | Enabled | Enabled | Enabled | Enabled | NA | Enabled | Enabled | Enabled | Enabled | Enabled | Enabled |  | Enabled | Backlog
AHU | AHU-12 | Cooling Valve Passing | Warning |  | Enabled | Enabled | Enabled | Enabled | NA | Enabled | Enabled | Enabled | Enabled | Enabled | Enabled |  | NA | Enabled
AHU | AHU-13 | Cooling Valve Hunting | Alert |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
AHU | AHU-14 | Not Achieving Supply Temp (Clg) | Warning |  | Enabled | Enabled | Enabled | Backlog | NA | Enabled | Enabled | Enabled | Enabled | Enabled | Enabled |  | NA | Enabled
AHU | AHU-15 | Heating and Cooling Together | Warning |  | Enabled | Enabled | Enabled | Enabled | NA | Enabled | Enabled | Enabled | NA | Enabled | Enabled |  | NA | Enabled
AHU | AHU-16 | Free Cooling Not Used | Alert |  | Backlog | Backlog | Backlog | Backlog | NA | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog |  | Backlog | Backlog
AHU | AHU-17 | Economising in Wrong Conditions | Warning |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
AHU | AHU-18 | OA Damper Not Responding | Warning |  | Backlog | Backlog | Backlog | Backlog | NA | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog
AHU | AHU-19 | Minimum Fresh Air Not Maintained | Warning |  | NA | NA | NA | NA | NA | NA | NA
AHU | AHU-20 | Duct Pressure Not Achieved | Warning |  | Backlog | Backlog | Backlog | Backlog | NA | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog
AHU | AHU-21 | Fan Speed Saturated | Alert |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
AHU | AHU-22 | Fan Speed Not Following Command | Warning |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
AHU | AHU-23 | Filter Requires Replacement | Alert |  | Backlog | Backlog | Backlog | Backlog | NA | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog
AHU | AHU-24 | Filter Sensor Suspect | Alert |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
AHU | AHU-25 | Extract Fan Failed | Critical |  | Enabled | Enabled | Enabled | Enabled | NA | Enabled | Enabled | Enabled | Enabled | Enabled | Enabled |  | Enabled | Enabled
AHU | AHU-26 | Frost Stat Tripped | Warning |  | Enabled | Enabled | Enabled | Enabled | NA | Enabled | Enabled | Enabled | Enabled | Enabled | Enabled |  | Enabled | Enabled
AHU | AHU-27 | Coil Valve Not Responding | Warning |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
AHU | AHU-28 | Heat Recovery Device Failure | Warning |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
AHU | AHU-29 | High Space CO2 | Warning |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
AHU | AHU-30 | Space Humidity Out of Bounds | Alert |  | Backlog | NA | NA | NA | NA | NA | NA | Backlog | NA | NA | NA | NA | NA | NA
AHU | AHU-31 | Return Air Temp Drift | Alert |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
AHU | AHU-32 | Night Purge Opportunity Missed | Alert |  | Backlog | Backlog | Backlog | Backlog | NA | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog |  | Backlog | Backlog
FCU | FCU-01 | Fan Failed | Critical |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
FCU | FCU-02 | Fan Running in Hand | Warning |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
FCU | FCU-03 | Sensor Flatlined | Warning |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
FCU | FCU-04 | Sensor Reading Implausible | Warning |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
FCU | FCU-05 | Running Outside Schedule | Warning |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
FCU | FCU-06 | Zone Temp Not Achieved (Clg) | Warning |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
FCU | FCU-07 | Zone Temp Not Achieved (Htg) | Warning |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
FCU | FCU-08 | Heating and Cooling Together | Warning |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
FCU | FCU-09 | Valve Passing | Warning |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
FCU | FCU-10 | Setpoint Outside Policy | Info |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
FCU | FCU-11 | Zone Temperature Oscillating | Info |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
VAV | VAV-01 | Airflow Not Achieved | Warning |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
VAV | VAV-02 | Airflow With Damper Closed | Warning |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
VAV | VAV-03 | Damper Not Responding | Warning |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
VAV | VAV-04 | Zone Temp Not Achieved (Clg) | Warning |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
VAV | VAV-05 | Zone Temp Not Achieved (Htg) | Warning |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
VAV | VAV-06 | Reheat Valve Passing | Warning |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
VAV | VAV-07 | Excessive Reheat | Alert |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
VAV | VAV-08 | Sensor Flatlined | Warning |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
VAV | VAV-09 | Setpoint Outside Policy | Info |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
VAV | VAV-10 | Airflow During Unoccupied | Alert |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Chiller | CH-01 | Failed to Start | Critical |  | Blocked | Enabled | Enabled | Enabled | NA | Enabled | NA | Enabled | Blocked | NA | NA |  | NA | Blocked
Chiller | CH-02 | Running in Hand | Warning |  | Backlog | Backlog | Backlog | Backlog | NA | Backlog | NA | Backlog | Backlog | Backlog | NA |  | NA | Backlog
Chiller | CH-03 | Short Cycling | Warning |  | Backlog | Backlog | Backlog | Backlog | NA | Backlog | NA | Backlog | Backlog | Backlog | NA |  | NA | Backlog
Chiller | CH-04 | General Alarm Active | Critical |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Chiller | CH-05 | CHW Flow Temp Not Achieved | Warning |  | Backlog | Backlog | Backlog | Backlog | NA | Backlog | NA | Backlog | Backlog | Backlog | NA |  | NA | Backlog
Chiller | CH-06 | Low Evaporator dT | Alert |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Chiller | CH-07 | High Condenser Temp | Warning |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Chiller | CH-08 | Condenser Approach High | Alert |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Chiller | CH-09 | Poor Efficiency vs Baseline | Alert |  | NA | NA | NA | NA | NA | NA | NA |  |  |  | NA |  | NA
Chiller | CH-10 | Sensor Flatlined | Warning |  | Backlog | Backlog | Backlog | Backlog | NA | Backlog | NA | Backlog | Backlog | Backlog | NA |  | NA | Backlog
Chiller | CH-11 | Running Outside Schedule | Warning |  | Backlog | Backlog | Backlog | Backlog | NA | Backlog | NA | Backlog | Backlog | Backlog | NA |  | NA | Backlog
Chiller | CH-12 | Excess Chillers Staged | Alert |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Chiller | CH-13 | All Chillers Failed / Cooling Unavailable | Critical | Y | Backlog | Enabled | Enabled | Enabled | NA | Backlog | NA | Enabled | Backlog | Backlog | NA |  | NA | Backlog
Chiller | CH-14 | Partial Chiller Failure (Redundancy Reduced) | Warning |  | Backlog | Backlog | Backlog | Backlog | NA | Backlog | NA | Backlog | Backlog | Backlog | NA |  | NA | Backlog
Chiller | CH-15 | OAT Hold-Off Active | Info |  | Backlog | Backlog | Backlog | Backlog | NA | Backlog | NA | Backlog | Backlog | Backlog | NA |  | NA | Backlog
Chiller | CH-16 | Evaporator Approach High | Alert |  | NA | NA | NA | NA | NA | NA | NA |  |  |  | NA |  | NA
Boiler | BLR-01 | Failed to Start | Critical |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Boiler | BLR-02 | Lockout / Alarm Active | Critical |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Boiler | BLR-03 | Running in Hand | Warning |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Boiler | BLR-04 | Short Cycling | Warning |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Boiler | BLR-05 | Flow Temp Not Achieved | Warning |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Boiler | BLR-06 | Return Temp Below Protection | Warning |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Boiler | BLR-07 | Low dT Across Boiler | Alert |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Boiler | BLR-08 | Sensor Flatlined | Warning |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Boiler | BLR-09 | Running Outside Schedule | Warning |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Boiler | BLR-10 | Excess Boilers Staged | Alert |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Boiler | BLR-11 | Partial Boiler Failure (Redundancy Reduced) | Warning |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Pumps (Primary) | PMP-01 | Pump Failed | Warning |  | Backlog | Backlog | Backlog | Backlog | NA | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog
Pumps (Primary) | PMP-02 | Running in Hand | Warning |  | Backlog | Backlog | Backlog | Backlog | NA | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog
Pumps (Primary) | PMP-03 | Short Cycling | Warning |  | Backlog | Backlog | Backlog | Backlog | NA | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog
Pumps (Primary) | PMP-04 | Pressure Not Achieved at Full Speed | Warning |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Pumps (Primary) | PMP-05 | Speed Saturated | Alert |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Pumps (Primary) | PMP-06 | No Flow Evidence While Running | Warning |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Pumps (Primary) | PMP-07 | Duty/Standby Not Rotating | Alert |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Pumps (Primary) | PMP-08 | All Pumps on Circuit Failed | Critical | Y | Backlog | Enabled | Backlog | Backlog | NA | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog
Pumps (Primary) | PMP-09 | Partial Pump Failure (Redundancy Reduced) | Warning |  | Backlog | Backlog | Backlog | Backlog | NA | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog
Cooling Tower | CT-01 | Fan Failed | Critical |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Cooling Tower | CT-02 | Fan Running in Hand | Warning |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Cooling Tower | CT-03 | CW Temp Not Achieved | Warning |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Cooling Tower | CT-04 | Approach Temp High | Alert |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Cooling Tower | CT-05 | Sensor Flatlined | Warning |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Cooling Tower | CT-06 | Running Outside Schedule/Season | Alert |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Cooling Tower | CT-07 | Basin Heater Fault | Warning |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Cooling Tower | CT-08 | Partial Tower Fan / Cell Failure (Redundancy Reduced) | Warning |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Metering & Energy | MTR-01 | Meter Not Reporting | Warning |  | Blocked | Blocked | Blocked | Blocked | NA | Blocked | Blocked | Blocked | Blocked | Blocked | Blocked | Blocked | Blocked | Blocked
Metering & Energy | MTR-02 | Meter Reading Implausible | Warning |  | Blocked | Blocked | Blocked | Blocked | NA | Blocked | Blocked | Blocked | Blocked | Blocked | Blocked | Blocked | Blocked | Blocked
Metering & Energy | MTR-03 | Out-of-Hours Baseload High | Alert |  | Blocked | Blocked | Blocked | Blocked | NA | Blocked | Blocked | Blocked | Blocked | Blocked | Blocked | Blocked | Blocked | Blocked
Metering & Energy | MTR-04 | Demand Spike vs Baseline | Alert |  | Blocked | Blocked | Blocked | Blocked | NA | Blocked | Blocked | Blocked | Blocked | Blocked | Blocked | Blocked | Blocked | Blocked
Metering & Energy | MTR-05 | Main vs Submeter Imbalance | Alert |  | Blocked | Blocked | Blocked | Blocked | NA | Blocked | Blocked | Blocked | Blocked | Blocked | Blocked | Blocked | Blocked | Blocked
Metering & Energy | MTR-06 | Gas Use With No Heat Demand | Alert |  | Blocked | Blocked | Blocked | Blocked | NA | Blocked | Blocked | Blocked | Blocked | Blocked | Blocked | Blocked | Blocked | Blocked
Metering & Energy | MTR-07 | HVAC Energy While Unoccupied | Alert |  | Blocked | Blocked | Blocked | Blocked | NA | Blocked | Blocked | Blocked | Blocked | Blocked | Blocked | Blocked | Blocked | Blocked
Metering & Energy | MTR-08 | Make-Up Water High Usage | Alert |  | Blocked | Blocked | Blocked | Blocked | NA | Blocked | Blocked | Blocked | Blocked | Blocked | Blocked | Blocked | Blocked | Blocked
BMS Health | BMS-01 | Device Offline | alert |  | Backlog | Backlog | Backlog | Backlog | NA | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog
BMS Health | BMS-02 | Points Stale | Warning |  | Backlog | Backlog | Backlog | Backlog | NA | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog
BMS Health | BMS-03 | Excessive Overrides Active | Alert |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
BMS Health | BMS-04 | Schedule Missing or Disabled | Warning |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
BMS Health | BMS-05 | Sensor Implausible (Global Sweep) | Warning |  | Backlog | Backlog | Backlog | Backlog | NA | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog
BMS Health | BMS-06 | Controller Time Drift | Alert |  | NA | NA | NA | NA | NA | NA
Boosted Cold Water | BCW-01 | Booster Pump Failed | Critical |  | Backlog | Backlog | Backlog | Backlog | NA | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog
Boosted Cold Water | BCW-02 | Booster Set Unavailable | Critical |  | Backlog | Backlog | Backlog | Backlog | NA | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog
Boosted Cold Water | BCW-03 | Low System Pressure | Critical |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Boosted Cold Water | BCW-04 | High System Pressure | Warning |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Boosted Cold Water | BCW-05 | Excessive Pump Cycling | Warning |  | Backlog | Backlog | Backlog | Backlog | NA | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog
Boosted Cold Water | BCW-06 | Duty/Standby Not Rotating | Alert |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Boosted Cold Water | BCW-07 | Tank Level Low | Critical |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Boosted Cold Water | BCW-08 | Tank Level High / Overflow Risk | Warning |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Boosted Cold Water | BCW-09 | Continuous Run With No Demand | Alert |  | Backlog | Backlog | Backlog | Backlog | NA | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog
Boosted Cold Water | BCW-10 | Sensor Flatlined | Warning |  | Backlog | Backlog | Backlog | Backlog | NA | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog
Boosted Cold Water | BCW-11 | Partial Booster Pump Failure (Redundancy Reduced) | Warning |  | Backlog | Backlog | Backlog | Backlog | NA | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog
Fire Alarm Interface | FA-01 | Panel Fault Signal Active | Critical |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Backlog | NA | NA | NA | NA
Fire Alarm Interface | FA-02 | Panel Interface Offline | Critical |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Fire Alarm Interface | FA-03 | Isolation Active Too Long | Warning |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Fire Alarm Interface | FA-04 | Panel On Battery / Mains Fail | Warning |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Fire Alarm Interface | FA-05 | Alarm Signal Active | Critical | Y | Backlog | Enabled | Backlog | Backlog | NA | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog
Generator | GEN-01 | Failed to Start on Demand | Critical | Y | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Backlog | NA | NA | NA
Generator | GEN-02 | Common Alarm Active | Critical | Y | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  | NA | NA | NA
Generator | GEN-03 | Not in Auto | Critical |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  | NA | NA | NA
Generator | GEN-04 | Low Fuel Level | Warning |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  | NA | NA | NA
Generator | GEN-05 | Battery / Charger Fault | Warning |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  | NA | NA | NA
Generator | GEN-06 | Block Heater Fault | Warning |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  | NA | NA | NA
Generator | GEN-07 | Running Unexpectedly | Warning | Y | Backlog | Backlog | Backlog | Backlog | NA | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | NA | NA
Generator | GEN-08 | Test Run Missed | Alert |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  | NA | NA | NA
Generator | GEN-09 | Status Flatlined | Warning |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  | NA | NA | NA
Generator | GEN-10 | Partial Generator Failure (Redundancy Reduced) | Warning |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  | NA | NA | NA
ACB | ACB-01 | Breaker Tripped | Critical | Y | Backlog | Backlog | Backlog | Backlog | NA | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog
ACB | ACB-02 | Breaker Open Unexpectedly | Critical | Y | Backlog | Backlog | Backlog | Backlog | NA | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog
ACB | ACB-03 | Protection Unit Fault | Warning |  | NA | NA | NA | NA | NA | NA
ACB | ACB-04 | Not in Remote/Auto | Warning |  | NA | NA | NA | NA | NA | NA
ACB | ACB-05 | Comms Lost to Breaker | Warning |  | Backlog | Backlog | Backlog | Backlog | NA | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog
ATS | ATS-01 | Transferred to Alternate Source | Critical |  | Backlog | Backlog | Backlog | Backlog | NA | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog
ATS | ATS-02 | Failed to Transfer | Critical |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
ATS | ATS-03 | Not in Auto | Critical |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
ATS | ATS-04 | Failed to Retransfer | Warning |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
ATS | ATS-05 | Common Fault Active | Warning |  | Backlog | Backlog | Backlog | Backlog | NA | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog
ATS | ATS-06 | Comms Lost | Warning |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Calorifier / DHW | CAL-01 | Storage Temp Below Safe Minimum | Critical | Y | Backlog | Enabled | Backlog | Backlog | NA | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog |  | NA | Backlog
Calorifier / DHW | CAL-02 | Storage Temp Sensor Flatlined | Warning |  | Backlog | Backlog | Backlog | Backlog | NA | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog |  | NA | Backlog
Calorifier / DHW | CAL-03 | DHW Return Temp Low | Warning |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Calorifier / DHW | CAL-04 | Pasteurisation Cycle Missed | Alert |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Calorifier / DHW | CAL-05 | Partial Calorifier Failure (Redundancy Reduced) | Warning |  | Backlog | Backlog | Backlog | Backlog | NA | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog |  | NA | Backlog
District Energy | DE-01 | District LTHW Supply Failure | Critical | Y | Backlog | Enabled | Backlog | Backlog | NA | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog
District Energy | DE-02 | District CHWS Supply Failure | Critical | Y | Backlog | Backlog | Backlog | Backlog | NA | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | NA | NA | Backlog | NA | NA
District Energy | DE-03 | District Supply Temp Degraded | Warning |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
District Energy | DE-04 | Heat Meter Not Reporting | Warning |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
District Energy | DE-05 | LTHW Return Temp High (Network Penalty) | Alert |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
District Energy | DE-06 | CHWS Return Temp Low (Poor dT) | Alert |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Pressurisation Unit | PU-01 | Unit Fault / Failure | Critical | Y | Backlog | Backlog | Backlog | Backlog | NA | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog
Pressurisation Unit | PU-02 | System Pressure Low | Critical |  | Backlog | Enabled | Backlog | Backlog | NA | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | NA
Pressurisation Unit | PU-03 | System Pressure High | Warning |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Pressurisation Unit | PU-04 | Excessive Top-Up Activity | Alert |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Degasser | DG-01 | Degasser Fault | Warning | Y | Backlog | Backlog | Backlog | Backlog | NA | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog
Degasser | DG-02 | Not Running to Schedule | Alert |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Sump Pump | SP-01 | High Level Alarm | Critical | Y | Backlog | Enabled | Backlog | Backlog | NA | Backlog | Backlog | Backlog | NA | NA | Backlog | Backlog | Backlog | NA
Sump Pump | SP-02 | Pump Failed | Critical |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Sump Pump | SP-03 | All Pumps Failed | Critical |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Sump Pump | SP-04 | Excessive Cycling | Alert |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Sump Pump | SP-05 | Partial Sump Pump Failure (Redundancy Reduced) | Warning |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Leak Detection | LD-01 | Leak Detected | Critical | Y | Backlog | Enabled | Backlog | Backlog | NA | Backlog | Backlog | Backlog | NA | NA | NA |  | Backlog | NA
Leak Detection | LD-02 | Panel / Sensor Fault | Warning |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Leak Detection | LD-03 | Zone Isolated Too Long | Alert |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Refrigerant Leak | RL-01 | Refrigerant Leak Detected | Critical | Y | Backlog | NA | Backlog | Backlog | NA | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Blocked | Blocked
Refrigerant Leak | RL-02 | Detector / Panel Fault | Warning |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Blocked | Blocked
Smoke Control | SC-01 | Pressurisation / Smoke Fan Failed | Critical |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Smoke Control | SC-02 | System Fault Active | Warning |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Smoke Control | SC-03 | Test Run Missed | Alert |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Heat Exchanger (PHX) | HX-01 | Delta-T Deviation Across PHX | Alert |  | Backlog | Backlog | Backlog | Backlog | NA | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog
Heat Exchanger (PHX) | HX-02 | Approach Temperature High | Alert |  | Backlog | Backlog | Backlog | Backlog | NA | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog | Backlog
Pumps (Secondary) | SPMP-01 | Secondary Pump Failed | Critical
Pumps (Secondary) | SPMP-02 | Running in Hand | Warning
Pumps (Secondary) | SPMP-03 | Short Cycling | Warning
Pumps (Secondary) | SPMP-04 | No Flow Evidence While Running | Warning
Pumps (Secondary) | SPMP-05 | Duty/Standby Not Rotating | Alert
Pumps (Secondary) | SPMP-06 | All Secondary Pumps on Circuit Failed | Critical | Y
Pumps (Secondary) | SPMP-07 | Partial Pump Failure (Redundancy Reduced) | Warning
Pumps (Secondary) | SPMP-08 | Pressure Not Achieved at Full Speed | Warning
Pumps (Secondary) | SPMP-09 | Speed Saturated (Running at Max) | Alert
Pumps (Secondary) | SPMP-10 | Running at Minimum Speed | Alert
Pumps (Secondary) | SPMP-11 | dP Control Sensor Flatlined | Warning
Pumps (Secondary) | SPMP-12 | Staging Not Responding to Demand | Alert

## Key
KCE ESTATE FDD REGISTER v3.3 — BGIS RCC · companion to the RCC FDD Standard (v1.0)
One row per FDD concept, one column per building. Each status cell has a dropdown.
LIFECYCLE STATUSES
Backlog — in scope, not started. Built — routine exists per design record. Configured — tuned, named, routed.
Enabled — live in KODE and operational. Validated — completed the tuning and assurance period; fully assured.
Blocked — in scope but required data does not exist on the building. NA — feature absent; does not apply.
FDDs satisfied by an existing KODE Event follow the same lifecycle and are marked Validated once confirmed suitable.
COVERAGE MEASURES
Live coverage reflects FDD concepts that are active in KODE through an enabled or validated routine.
Validated coverage is tracked separately and represents routines that have completed the tuning and assurance period.
In Scope = Backlog + Built + Configured + Enabled + Validated + Blocked. Unassessed = blank cells.
Live Coverage % = Live ÷ In Scope. Validated Coverage % = Validated ÷ In Scope.
The RCC Coverage Dashboard reads this file locally — keep the sheet name and layout intact.