## Fault Tables
Equipment | Ref | Fault | Severity | OOH | Applies when | Data needed | Design intent & typical defaults | Notes (working)
AHU | AHU-01 | Supply Fan Failed | Critical | Y | Always | fan_cmd, fan_status | Commanded ON, 90s ramp grace, no proof for 5 min. Parent fault: suppresses the unit's downstream alerts.
AHU | AHU-02 | Fan Running in Hand | Warning |  | Always | fan_cmd, fan_status | Commanded OFF >= 5 min, status ON for 30 min.
AHU | AHU-03 | Fan Short Cycling | Warning |  | Always | fan_status | > 4 starts per rolling hour, 2 consecutive hours.
AHU | AHU-04 | Sensor Flatlined | Warning |  | Always | each bound analog | No change beyond deadband for 4 h while running. Suppresses alerts using that point.
AHU | AHU-05 | Sensor Reading Implausible | Warning |  | Always | each bound analog | Outside plausibility band (e.g. SAT -5 to 60 C) for 30 min.
AHU | AHU-06 | Running Outside Schedule | Warning |  | Always | fan_status, occupancy schedule | ON >= 60 min beyond schedule plus after-hours allowance.
AHU | AHU-07 | Failed to Start on Schedule | Critical |  | Always | schedule, fan_status | Occupied per schedule, no proof within 15 min of expected start.
AHU | AHU-08 | Excessive Continuous Runtime | Alert |  | Always | fan_status | Continuous run > 24 h where unit not designated 24/7.
AHU | AHU-09 | Heating Valve Passing | Warning |  | Heating coil | htg_valve, SAT, MAT/RAT | Valve < 2%, fan ON, SAT > MAT + 3 C for 60 min.
AHU | AHU-10 | Heating Valve Hunting | Alert |  | Heating coil | htg_valve | Command reversals > 6/hr with span > 20%, 2 h.
AHU | AHU-11 | Not Achieving Supply Temp (Htg) | Warning |  | Heating coil | SAT, SAT_sp, htg_valve | Valve >= 95%, SAT < SP - 2 C for 45 min, occupied.
AHU | AHU-12 | Cooling Valve Passing | Warning |  | Cooling coil | clg_valve, SAT, MAT/RAT | Valve < 2%, fan ON, SAT < MAT - 3 C for 60 min.
AHU | AHU-13 | Cooling Valve Hunting | Alert |  | Cooling coil | clg_valve | As heating valve hunting, cooling valve.
AHU | AHU-14 | Not Achieving Supply Temp (Clg) | Warning |  | Cooling coil | SAT, SAT_sp, clg_valve | Valve >= 95%, SAT > SP + 2 C for 45 min, occupied.
AHU | AHU-15 | Heating and Cooling Together | Warning |  | Both coils | htg_valve, clg_valve | Both > 10% concurrently for 30 min, fan ON, 30 min past start.
AHU | AHU-16 | Free Cooling Not Used | Alert |  | Economizer | OAT, RAT, oa_damper, cooling demand | Cooling cmd > 15%, OAT < RAT - 2 C, OAT > 4 C, damper < 25%, 45 min. Use enthalpy comparison where humidity sensors exist.
AHU | AHU-17 | Economising in Wrong Conditions | Warning |  | Economizer | OAT, RAT, oa_damper | Damper > minimum while OAT > RAT + 1 C for 45 min.
AHU | AHU-18 | OA Damper Not Responding | Warning |  | Economizer | oa_damper, MAT, OAT, RAT | Command change > 30%, MAT fails to move toward expected mix, 30 min.
AHU | AHU-19 | Minimum Fresh Air Not Maintained | Warning |  | Economizer | oa_damper (+ MAT or OA flow) | Occupied, damper < configured minimum for 30 min.
AHU | AHU-20 | Duct Pressure Not Achieved | Warning |  | VFD + static sensor | static_p, static_sp, fan_speed | Speed >= 95%, static < SP - tolerance for 30 min.
AHU | AHU-21 | Fan Speed Saturated | Alert |  | VFD | fan_speed | >= 95% for > 4 h occupied. Sizing / setpoint lead indicator.
AHU | AHU-22 | Fan Speed Not Following Command | Warning |  | VFD | speed_cmd, speed_fb | ¦cmd - feedback¦ > 10% for 15 min.
AHU | AHU-23 | Filter Requires Replacement | Alert |  | Filter dP sensor | filter_dp, fan_status | dP > threshold at representative speed for 2 h. Feeds PPM, not dispatch.
AHU | AHU-24 | Filter Sensor Suspect | Alert |  | Filter dP sensor | filter_dp, fan speed | dP near zero with fan at speed for 2 h.
AHU | AHU-25 | Extract Fan Failed | Critical |  | Extract fan fitted | ext_fan_cmd, ext_fan_status | Commanded ON, 90s ramp grace, no proof for 5 min.
AHU | AHU-26 | Frost Stat Tripped | Warning |  | Frost stat point visible | freeze stat status | Trip active for 5 min. Unit held off — check coil protection, valve positions, glycol.
AHU | AHU-27 | Coil Valve Not Responding | Warning |  | Any coil | valve cmd, SAT | Command change > 30%, SAT fails to move in the expected direction for 30 min (stuck / failed actuator).
AHU | AHU-28 | Heat Recovery Device Failure | Warning |  | Heat recovery fitted | device status or temps both sides | Device running with no temperature effectiveness for 60 min, or fault point active.
AHU | AHU-29 | High Space CO2 | Warning |  | CO2 sensor | zone CO2 | Above limit (e.g. 1200 ppm) for 30 min occupied. Ventilation shortfall.
AHU | AHU-30 | Space Humidity Out of Bounds | Alert |  | Humidity sensor | zone RH | Outside band (e.g. 30–65%) for 2 h occupied.
AHU | AHU-31 | Return Air Temp Drift | Alert |  | RAT sensor | RAT, zone temps | RAT diverging from zone average by > 3 C for 2 h (placement / stratification / bypass).
AHU | AHU-32 | Night Purge Opportunity Missed | Alert |  | Night purge strategy | OAT, zone temps, fan status | Favourable overnight conditions, purge not run, pre-cooling demand next morning.
FCU | FCU-01 | Fan Failed | Critical |  | Fan proof exists | fan_cmd, fan_status | Commanded ON, no proof for 5 min. No proof point on the unit = Blocked.
FCU | FCU-02 | Fan Running in Hand | Warning |  | Fan proof exists | fan_cmd, fan_status | Commanded OFF >= 5 min, status ON for 30 min.
FCU | FCU-03 | Sensor Flatlined | Warning |  | Always | each bound analog | No change beyond deadband for 4 h.
FCU | FCU-04 | Sensor Reading Implausible | Warning |  | Always | each bound analog | Outside plausibility band for 30 min.
FCU | FCU-05 | Running Outside Schedule | Warning |  | Always | fan_status/cmd, schedule | Running >= 60 min beyond schedule.
FCU | FCU-06 | Zone Temp Not Achieved (Clg) | Warning |  | Cooling coil | zone_temp, zone_sp, clg_valve | Valve >= 95%, zone > SP + 2 C for 60 min, occupied.
FCU | FCU-07 | Zone Temp Not Achieved (Htg) | Warning |  | Heating coil | zone_temp, zone_sp, htg_valve | Valve >= 95%, zone < SP - 2 C for 60 min, occupied.
FCU | FCU-08 | Heating and Cooling Together | Warning |  | Both coils (4-pipe) | htg_valve, clg_valve | Both > 10% concurrently for 30 min.
FCU | FCU-09 | Valve Passing | Warning |  | Any coil + discharge/zone temp | valve cmd, discharge or zone temp | Valve < 2%, temperature trends the wrong way for 60 min.
FCU | FCU-10 | Setpoint Outside Policy | Info |  | Always | zone_sp | Setpoint outside policy band (e.g. 19-24 C) for 4 h. Often an occupant-adjustment / handover issue.
FCU | FCU-11 | Zone Temperature Oscillating | Info |  | Always | zone_temp | Sustained oscillation > ±1.5 C around setpoint over 4 h. Control tuning indicator.
VAV | VAV-01 | Airflow Not Achieved | Warning |  | Flow sensor | damper_cmd, flow, flow_sp | Damper >= 95%, flow < SP - tolerance for 30 min (starved box: check AHU static, upstream balancing).
VAV | VAV-02 | Airflow With Damper Closed | Warning |  | Flow sensor | damper_cmd, flow | Damper <= 5%, flow above minimum for 30 min (leaking damper).
VAV | VAV-03 | Damper Not Responding | Warning |  | Flow sensor | damper_cmd, flow | Command change > 30%, flow unchanged for 30 min.
VAV | VAV-04 | Zone Temp Not Achieved (Clg) | Warning |  | Always | zone_temp, zone_sp | Cooling call at max flow, zone > SP + 2 C for 60 min, occupied.
VAV | VAV-05 | Zone Temp Not Achieved (Htg) | Warning |  | Reheat | zone_temp, zone_sp, rht_valve | Reheat >= 95%, zone < SP - 2 C for 60 min, occupied.
VAV | VAV-06 | Reheat Valve Passing | Warning |  | Reheat + discharge temp | rht_valve, discharge_temp | Valve < 2%, discharge > entering + 3 C for 60 min.
VAV | VAV-07 | Excessive Reheat | Alert |  | Reheat | rht_valve, AHU cooling state | Reheat > 50% while AHU is cooling, 2 h. Sequence / energy waste indicator.
VAV | VAV-08 | Sensor Flatlined | Warning |  | Always | each bound analog | No change beyond deadband for 4 h.
VAV | VAV-09 | Setpoint Outside Policy | Info |  | Always | zone_sp | Setpoint outside policy band for 4 h.
VAV | VAV-10 | Airflow During Unoccupied | Alert |  | Flow sensor | flow, schedule | Flow above minimum while unoccupied for 60 min.
Chiller | CH-01 | Failed to Start | Critical |  | Always | enable_cmd, run_status | Enabled, no run proof within 10 min.
Chiller | CH-02 | Running in Hand | Warning |  | Always | enable_cmd, run_status | Not enabled >= 10 min, still running for 30 min.
Chiller | CH-03 | Short Cycling | Warning |  | Always | run_status | > 3 starts per hour for 2 h.
Chiller | CH-04 | General Alarm Active | Critical |  | Alarm point integrated | chiller alarm point | Alarm true for 5 min. Diagnosis directs to chiller HMI fault code.
Chiller | CH-05 | CHW Flow Temp Not Achieved | Warning |  | Always | chws_temp, chws_sp | Running, CHWS > SP + 1.5 C for 45 min.
Chiller | CH-06 | Low Evaporator dT | Alert |  | CHW flow + return temps | chws_temp, chwr_temp | dT < 60% of design at meaningful load for 2 h (low delta-T syndrome: valves, bypass, flow).
Chiller | CH-07 | High Condenser Temp | Warning |  | Condenser temps | cws/cond temp | Above threshold for 30 min while running. Check towers / condenser flow.
Chiller | CH-08 | Condenser Approach High | Alert |  | Condenser temps | cond temp, cwr temp | Approach > baseline + 3 C for 4 h (fouling indicator).
Chiller | CH-09 | Poor Efficiency vs Baseline | Alert |  | kW metering | chiller kW, cooling load | Specific power > baseline + 15% for 4 h at comparable load.
Chiller | CH-10 | Sensor Flatlined | Warning |  | Always | each bound analog | No change beyond deadband for 4 h while running.
Chiller | CH-11 | Running Outside Schedule | Warning |  | Always | run_status, schedule/season | Running >= 60 min beyond schedule or season flag.
Chiller | CH-12 | Excess Chillers Staged | Alert |  | Multiple chillers + load data | run statuses, combined load | N+1 machines running with combined load < 40% for 2 h (staging / sequencing).
Chiller | CH-13 | All Chillers Failed / Cooling Unavailable | Critical | Y | Multiple chillers | chiller run statuses, CHWS temp | No chiller proving while cooling enabled and CHWS temp rising for 15 min. Plant-level parent fault — the OOH call-out trigger.
Chiller | CH-14 | Partial Chiller Failure (Redundancy Reduced) | Warning |  | Multiple chillers | chiller statuses, demand | One machine failed or locked out while others carry the load. Service OK — resilience consumed.
Chiller | CH-15 | OAT Hold-Off Active | Info |  | OAT hold-off strategy | OAT, enable status | Chillers held off on OAT strategy. Informational; suppresses failure alerts during hold-off.
Chiller | CH-16 | Evaporator Approach High | Alert |  | Evap refrigerant/water temps | evap leaving water temp, evap refrigerant temp | Approach > baseline + 2 C for 4 h. Low refrigerant charge or evaporator fouling — the early warning before capacity loss.
Boiler | BLR-01 | Failed to Start | Critical |  | Always | enable_cmd, run/fire status | Enabled, no firing proof within 10 min.
Boiler | BLR-02 | Lockout / Alarm Active | Critical |  | Alarm point integrated | boiler alarm/lockout point | Alarm true for 5 min.
Boiler | BLR-03 | Running in Hand | Warning |  | Always | enable_cmd, run status | Not enabled >= 10 min, still firing for 30 min.
Boiler | BLR-04 | Short Cycling | Warning |  | Always | fire status | > 6 starts per hour for 2 h.
Boiler | BLR-05 | Flow Temp Not Achieved | Warning |  | Always | hws_temp, hws_sp | Firing, HWS < SP - 3 C for 45 min.
Boiler | BLR-06 | Return Temp Below Protection | Warning |  | Non-condensing plant | hwr_temp | Return < protection minimum (e.g. 55 C) for 30 min while firing (thermal shock / corrosion risk).
Boiler | BLR-07 | Low dT Across Boiler | Alert |  | Flow + return temps | hws_temp, hwr_temp | dT < 50% of design while firing for 2 h (flow / bypass issue).
Boiler | BLR-08 | Sensor Flatlined | Warning |  | Always | each bound analog | No change beyond deadband for 4 h.
Boiler | BLR-09 | Running Outside Schedule | Warning |  | Always | fire status, schedule/season | Firing >= 60 min beyond schedule or season flag.
Boiler | BLR-10 | Excess Boilers Staged | Alert |  | Multiple boilers | fire statuses, demand | Multiple boilers firing at low combined demand for 2 h.
Boiler | BLR-11 | Partial Boiler Failure (Redundancy Reduced) | Warning |  | Multiple boilers | boiler statuses, demand | One boiler failed or locked out while the remaining unit(s) carry the load. Service maintained — resilience reduced until repaired.
Pumps (Primary) | PMP-01 | Pump Failed | Critical |  | Always | pump_cmd, pump_status | Commanded ON, no proof for 2 min. Critical on primary circuits; consider Warning on tertiary.
Pumps (Primary) | PMP-02 | Running in Hand | Warning |  | Always | pump_cmd, pump_status | Commanded OFF >= 5 min, status ON for 30 min.
Pumps (Primary) | PMP-03 | Short Cycling | Warning |  | Always | pump_status | > 6 starts per hour for 2 h.
Pumps (Primary) | PMP-04 | Pressure Not Achieved at Full Speed | Warning |  | VSD + dP sensor | speed, dP, dP_sp | Speed >= 95%, dP < SP - tolerance for 30 min.
Pumps (Primary) | PMP-05 | Speed Saturated | Alert |  | VSD | speed | >= 95% for 4 h. Sizing / setpoint / valve-authority lead indicator.
Pumps (Primary) | PMP-06 | No Flow Evidence While Running | Warning |  | dP or flow sensor | status, dP/flow | Running with dP or flow near zero for 15 min (deadhead, closed valve, coupling).
Pumps (Primary) | PMP-07 | Duty/Standby Not Rotating | Alert |  | Duty/standby pair | both pump statuses | Same pump leading beyond rotation period (changeover failure; hidden standby faults).
Pumps (Primary) | PMP-08 | All Pumps on Circuit Failed | Critical | Y | Duty/standby pair | all pump statuses on circuit | No pump proving on a circuit with demand for 5 min. Circuit-level parent fault (primary / secondary / LTHW / CHWS loops) — the OOH call-out trigger.
Pumps (Primary) | PMP-09 | Partial Pump Failure (Redundancy Reduced) | Warning |  | Duty/standby pair | pump statuses | Standby carrying duty after a failure. Service maintained; resilience lost until repaired.
Cooling Tower | CT-01 | Fan Failed | Critical |  | Always | fan_cmd, fan_status | Commanded ON, no proof for 5 min.
Cooling Tower | CT-02 | Fan Running in Hand | Warning |  | Always | fan_cmd, fan_status | Commanded OFF >= 5 min, status ON for 30 min.
Cooling Tower | CT-03 | CW Temp Not Achieved | Warning |  | Always | cws_temp, cws_sp | CWS > SP + 2 C for 45 min with fans available.
Cooling Tower | CT-04 | Approach Temp High | Alert |  | OAT / wet-bulb data | cws_temp, OAT/wet-bulb | Approach > baseline + 3 C for 4 h (fill fouling, airflow, water distribution).
Cooling Tower | CT-05 | Sensor Flatlined | Warning |  | Always | each bound analog | No change beyond deadband for 4 h.
Cooling Tower | CT-06 | Running Outside Schedule/Season | Alert |  | Always | fan_status, schedule/season | Running >= 60 min beyond schedule or season flag.
Cooling Tower | CT-07 | Basin Heater Fault | Warning |  | Basin heater fitted | heater status, basin temp, OAT | OAT below threshold, heater not proving or basin temp falling toward freeze for 60 min. Winter freeze damage risk.
Cooling Tower | CT-08 | Partial Tower Fan / Cell Failure (Redundancy Reduced) | Warning |  | Multiple towers or fan cells | fan/cell statuses | One tower fan / cell failed or locked out while the remaining unit(s) carry the load. Service maintained — resilience reduced until repaired.
Metering & Energy | MTR-01 | Meter Not Reporting | Warning |  | Always | meter reading | No new data for 4 h.
Metering & Energy | MTR-02 | Meter Reading Implausible | Warning |  | Always | meter reading | Negative, rollback, or beyond physical maximum.
Metering & Energy | MTR-03 | Out-of-Hours Baseload High | Alert |  | Baseline available | interval consumption, schedule | Unoccupied consumption > baseline + 20% for 3 consecutive nights.
Metering & Energy | MTR-04 | Demand Spike vs Baseline | Alert |  | Baseline available | interval demand | Demand > baseline + 30% sustained for 2 h, no known cause.
Metering & Energy | MTR-05 | Main vs Submeter Imbalance | Alert |  | Submeter hierarchy | main + submeter readings | Sum of submeters drifts > 10% from main over 24 h (metering integrity).
Metering & Energy | MTR-06 | Gas Use With No Heat Demand | Alert |  | Gas meter + plant status | gas flow, heating plant status | Gas flow while heating plant off for 2 h.
Metering & Energy | MTR-07 | HVAC Energy While Unoccupied | Alert |  | HVAC submeter | HVAC kW, schedule | HVAC demand above floor while unoccupied for 2 h.
Metering & Energy | MTR-08 | Make-Up Water High Usage | Alert |  | Make-up meter | make-up water meter | Usage above baseline over 24 h. System leak indicator.
BMS Health | BMS-01 | Device Offline | Critical |  | Always | comms status | Device offline for 15 min. Suppresses all alerts on that device.
BMS Health | BMS-02 | Points Stale | Warning |  | Always | point updates | No value changes across device for 4 h while plant running.
BMS Health | BMS-03 | Excessive Overrides Active | Alert |  | Writable points | override states | More than N operator overrides active for 24 h.
BMS Health | BMS-04 | Schedule Missing or Disabled | Warning |  | Always | schedule binding | Scheduled asset with no active schedule bound.
BMS Health | BMS-05 | Sensor Implausible (Global Sweep) | Warning |  | Always | all analog sensors | Site-wide plausibility check; feeds data readiness score.
BMS Health | BMS-06 | Controller Time Drift | Alert |  | Clock readable | controller clock | Drift > 5 min vs reference (breaks schedule logic silently).
Boosted Cold Water | BCW-01 | Booster Pump Failed | Critical |  | Always | pump_cmd, pump_status | Duty pump commanded, no proof for 2 min.
Boosted Cold Water | BCW-02 | Booster Set Unavailable | Critical |  | Multi-pump set | all pump statuses / set fault | No pump available to run, or common set fault active, 2 min. Loss of water supply risk.
Boosted Cold Water | BCW-03 | Low System Pressure | Critical |  | Pressure sensor | system pressure | Below minimum for 5 min. Supply failure to outlets / risk to downstream plant.
Boosted Cold Water | BCW-04 | High System Pressure | Warning |  | Pressure sensor | system pressure | Above maximum for 15 min. PRV or transducer fault.
Boosted Cold Water | BCW-05 | Excessive Pump Cycling | Warning |  | Always | pump_status | > 10 starts per hour for 2 h. Classic failed accumulator vessel or system leak.
Boosted Cold Water | BCW-06 | Duty/Standby Not Rotating | Alert |  | Duty/standby pair | pump statuses | Same pump leading beyond rotation period; hidden standby faults.
Boosted Cold Water | BCW-07 | Tank Level Low | Critical |  | Level sensor | tank level | Below low limit for 5 min.
Boosted Cold Water | BCW-08 | Tank Level High / Overflow Risk | Warning |  | Level sensor | tank level | Above high limit for 15 min. Inlet valve failure.
Boosted Cold Water | BCW-09 | Continuous Run With No Demand | Alert |  | Always | pump_status | Running continuously through overnight low-demand period. Leak indicator.
Boosted Cold Water | BCW-10 | Sensor Flatlined | Warning |  | Always | each bound analog | No change beyond deadband for 4 h.
Boosted Cold Water | BCW-11 | Partial Booster Pump Failure (Redundancy Reduced) | Warning |  | Multi-pump set | pump statuses | One booster pump failed or locked out while the remaining unit(s) carry the load. Service maintained — resilience reduced until repaired.
Fire Alarm Interface | FA-01 | Panel Fault Signal Active | Critical |  | Always | panel fault output | Fault active for 5 min. NOTE: this monitors panel health via the BMS interface; it supplements and never replaces the regulated fire alarm response chain.
Fire Alarm Interface | FA-02 | Panel Interface Offline | Critical |  | Always | interface comms | No comms with the panel interface for 15 min. We are blind to panel status.
Fire Alarm Interface | FA-03 | Isolation Active Too Long | Warning |  | Isolation status visible | isolation status | Zone/device isolation active > 24 h. Typically left isolated after works.
Fire Alarm Interface | FA-04 | Panel On Battery / Mains Fail | Warning |  | Power status visible | panel power status | Running on battery for 15 min.
Fire Alarm Interface | FA-05 | Alarm Signal Active | Critical | Y | Always | panel alarm output | Immediate.
Generator | GEN-01 | Failed to Start on Demand | Critical | Y | Always | start_cmd, run_status | Start demanded, no run proof within 60 s.
Generator | GEN-02 | Common Alarm Active | Critical | Y | Alarm point | genset alarm point | Alarm true for 2 min. Diagnosis directs to genset controller code.
Generator | GEN-03 | Not in Auto | Critical |  | Mode status | mode switch position | Not in auto for 15 min. Set will not start on mains failure.
Generator | GEN-04 | Low Fuel Level | Warning |  | Fuel level sensor | fuel level | Below threshold (e.g. 50%) — escalate to Critical below run-time minimum.
Generator | GEN-05 | Battery / Charger Fault | Warning |  | Charger or battery point | charger status / battery V | Fault or low volts for 15 min. The most common cause of failed starts.
Generator | GEN-06 | Block Heater Fault | Warning |  | Heater or engine temp point | heater status / engine temp | Heater off or engine temp low for 2 h. Cold-start risk.
Generator | GEN-07 | Running Unexpectedly | Warning | Y | Always | run_status, mains status | Running with mains healthy and no test window for 15 min.
Generator | GEN-08 | Test Run Missed | Alert |  | Always | run history | No run recorded within the test period (e.g. monthly). Confirms the test regime actually happens.
Generator | GEN-09 | Status Flatlined | Warning |  | Always | each bound point | No updates from genset points for 4 h.
Generator | GEN-10 | Partial Generator Failure (Redundancy Reduced) | Warning |  | Multiple generator sets | set statuses, alarms | One generator failed or locked out while the remaining unit(s) carry the load. Service maintained — resilience reduced until repaired.
ACB | ACB-01 | Breaker Tripped | Critical | Y | Trip status | trip status | Trip active — immediate. Parent fault for downstream supply alerts.
ACB | ACB-02 | Breaker Open Unexpectedly | Critical | Y | Position status | open/closed status | Open while expected closed for 2 min.
ACB | ACB-03 | Protection Unit Fault | Warning |  | Fault point | trip unit fault | Fault active for 15 min. Protection integrity at risk.
ACB | ACB-04 | Not in Remote/Auto | Warning |  | Mode status | mode position | Left in local/manual for 60 min after works.
ACB | ACB-05 | Comms Lost to Breaker | Warning |  | Always | breaker comms | No comms for 15 min.
ATS | ATS-01 | Transferred to Alternate Source | Critical |  | Always | switch position | On generator/alternate — immediate. This is the mains-failure event notification.
ATS | ATS-02 | Failed to Transfer | Critical |  | Transfer cmd visible | transfer cmd, position | Transfer demanded, position unchanged within 30 s.
ATS | ATS-03 | Not in Auto | Critical |  | Mode status | mode position | Not in auto for 15 min. Will not transfer on mains failure.
ATS | ATS-04 | Failed to Retransfer | Warning |  | Always | mains status, position | Mains healthy for retransfer delay + 15 min, still on alternate.
ATS | ATS-05 | Common Fault Active | Warning |  | Fault point | ATS fault point | Fault active for 5 min.
ATS | ATS-06 | Comms Lost | Warning |  | Always | ATS comms | No comms for 15 min.
Calorifier / DHW | CAL-01 | Storage Temp Below Safe Minimum | Critical | Y | Always | storage temp | Below safe storage temp (e.g. 55 C) for 60 min. Legionella risk + loss of hot water.
Calorifier / DHW | CAL-02 | Storage Temp Sensor Flatlined | Warning |  | Always | storage temp | No change beyond deadband for 4 h. A flat sensor here hides a safety issue.
Calorifier / DHW | CAL-03 | DHW Return Temp Low | Warning |  | Return temp sensor | return temp | Below circulation minimum (e.g. 50 C) for 60 min.
Calorifier / DHW | CAL-04 | Pasteurisation Cycle Missed | Alert |  | Cycle visible in BMS | cycle status / temp history | No anti-legionella cycle completed within the scheduled period.
Calorifier / DHW | CAL-05 | Partial Calorifier Failure (Redundancy Reduced) | Warning |  | Multiple calorifiers | calorifier statuses, temps | One calorifier failed or locked out while the remaining unit(s) carry the load. Service maintained — resilience reduced until repaired.
District Energy | DE-01 | District LTHW Supply Failure | Critical | Y | LTHW connection | supply temp, dP/flow | Supply temp below threshold or dP collapsed for 15 min. Estate-level parent fault for heating.
District Energy | DE-02 | District CHWS Supply Failure | Critical | Y | CHWS connection | supply temp, dP/flow | Supply temp above threshold or dP collapsed for 15 min. Estate-level parent fault for cooling.
District Energy | DE-03 | District Supply Temp Degraded | Warning |  | Always | supply temp | Outside contract band for 60 min. Underperformance, not failure — evidence for the energy provider.
District Energy | DE-04 | Heat Meter Not Reporting | Warning |  | Heat meter integrated | meter reading | No new data for 4 h. Billing and performance-evidence integrity.
District Energy | DE-05 | LTHW Return Temp High (Network Penalty) | Alert |  | LTHW connection | LTHW return temp | Return temp above network target band for 4 h at load. Poor secondary dT — directly drives district energy penalty charges.
District Energy | DE-06 | CHWS Return Temp Low (Poor dT) | Alert |  | CHWS connection | CHWS return temp | Return temp below target band for 4 h at load. Low delta-T syndrome on the network connection — capacity wasted, penalties risked.
Pressurisation Unit | PU-01 | Unit Fault / Failure | Critical | Y | Always | unit fault point | Fault active for 5 min. Loss of system pressure cascades into boiler/chiller lockouts.
Pressurisation Unit | PU-02 | System Pressure Low | Critical |  | Pressure sensor | system pressure | Below minimum for 5 min.
Pressurisation Unit | PU-03 | System Pressure High | Warning |  | Pressure sensor | system pressure | Above maximum for 15 min.
Pressurisation Unit | PU-04 | Excessive Top-Up Activity | Alert |  | Top-up/pump count visible | top-up events | Top-up frequency above baseline over 24 h. System leak indicator.
Degasser | DG-01 | Degasser Fault | Warning | Y | Always | fault point / status | Fault active for 15 min. Air in system degrades circulation and corrodes plant.
Degasser | DG-02 | Not Running to Schedule | Alert |  | Run status | run status, schedule | No run within the expected cycle period.
Sump Pump | SP-01 | High Level Alarm | Critical | Y | Always | high level float/sensor | Active for 2 min. Flood risk — the OOH call-out trigger.
Sump Pump | SP-02 | Pump Failed | Critical |  | Pump status available | pump_cmd, pump_status | Commanded / level demand, no proof for 2 min.
Sump Pump | SP-03 | All Pumps Failed | Critical |  | Multi-pump sump | all pump statuses | No pump available with level demand for 2 min.
Sump Pump | SP-04 | Excessive Cycling | Alert |  | Always | pump_status | Starts per hour above baseline for 24 h. Rising inflow / failing check valve.
Sump Pump | SP-05 | Partial Sump Pump Failure (Redundancy Reduced) | Warning |  | Multi-pump sump | pump statuses | One sump pump failed or locked out while the remaining unit(s) carry the load. Service maintained — resilience reduced until repaired.
Leak Detection | LD-01 | Leak Detected | Critical | Y | Always | zone alarm point | Zone alarm active — immediate.
Leak Detection | LD-02 | Panel / Sensor Fault | Warning |  | Always | panel fault point | Fault active for 15 min. Detection integrity.
Leak Detection | LD-03 | Zone Isolated Too Long | Alert |  | Isolation visible | zone isolation status | Isolation active > 24 h — typically left after works.
Refrigerant Leak | RL-01 | Refrigerant Leak Detected | Critical | Y | Always | gas sensor / panel alarm | Alarm active — immediate. Safety + F-Gas obligation.
Refrigerant Leak | RL-02 | Detector / Panel Fault | Warning |  | Always | panel fault point | Fault active for 15 min.
Smoke Control | SC-01 | Pressurisation / Smoke Fan Failed | Critical |  | Always | fan_cmd, fan_status | Demanded (run or test), no proof within 60 s. Health monitoring via BMS interface — supplements, never replaces, the regulated smoke control system.
Smoke Control | SC-02 | System Fault Active | Warning |  | Fault point | system fault point | Fault active for 15 min.
Smoke Control | SC-03 | Test Run Missed | Alert |  | Run history visible | run history | No test run within the scheduled period.
Heat Exchanger (PHX) | HX-01 | Delta-T Deviation Across PHX | Alert |  | Both-side temps | flow/return temps both sides | Primary or secondary dT < 60% of design at load for 2 h. Fouling / flow imbalance.
Heat Exchanger (PHX) | HX-02 | Approach Temperature High | Alert |  | Both-side temps | primary + secondary flow temps | Approach > baseline + 2 C for 4 h. Fouling indicator.
Pumps (Secondary) | SPMP-01 | Secondary Pump Failed | Critical |  | Always | spump_cmd, spump_status | Commanded ON, no proof for 2 min. Loss of a secondary (distribution) pump — falls to standby if fitted, otherwise loss of flow to the served loop.
Pumps (Secondary) | SPMP-02 | Running in Hand | Warning |  | Always | spump_cmd, spump_status | Commanded OFF >= 5 min, status ON for 30 min. Secondary pump left in hand after works — bypasses dP control and staging.
Pumps (Secondary) | SPMP-03 | Short Cycling | Warning |  | Always | spump_status | > 6 starts per hour for 2 h. On a staged secondary set this usually means a staging deadband that is too tight or a dP setpoint fighting the valves.
Pumps (Secondary) | SPMP-04 | No Flow Evidence While Running | Warning |  | dP or flow sensor | spump_status, dP/flow | Running with dP or flow near zero for 15 min (deadhead, closed isolation, coupling failure) — distribution not actually circulating.
Pumps (Secondary) | SPMP-05 | Duty/Standby Not Rotating | Alert |  | Duty/standby set | all secondary pump statuses | Same secondary pump leading beyond the rotation period — changeover failure hides a dormant standby fault until the duty pump drops.
Pumps (Secondary) | SPMP-06 | All Secondary Pumps on Circuit Failed | Critical | Y | Duty/standby set | all secondary pump statuses on circuit | No secondary pump proving on a distribution circuit with demand for 5 min. Circuit-level parent fault — total loss of flow to the served loop (LTHW/CHW distribution). The OOH call-out trigger for the secondary side.
Pumps (Secondary) | SPMP-07 | Partial Pump Failure (Redundancy Reduced) | Warning |  | Duty/standby set | secondary pump statuses | Standby carrying duty after a secondary pump failure. Distribution maintained; resilience lost until repaired.
Pumps (Secondary) | SPMP-08 | Pressure Not Achieved at Full Speed | Warning |  | VSD + dP sensor | speed, dP, dP_sp | Speed >= 95%, dP < setpoint − tolerance for 30 min. The secondary set is at capacity and still under its differential-pressure target — undersized, blocked, or too many open branches.
Pumps (Secondary) | SPMP-09 | Speed Saturated (Running at Max) | Alert |  | VSD | speed | >= 95% for 4 h. Lead indicator on the secondary set — sizing, dP setpoint or valve-authority issue building toward a pressure-not-achieved fault.
Pumps (Secondary) | SPMP-10 | Running at Minimum Speed | Alert |  | VSD | speed, dP, dP_sp | Speed pinned at the minimum limit with demand present for 4 h. Oversized secondary pump, dP setpoint set too low, or two-port valves barely modulating — wasted energy and poor authority.
Pumps (Secondary) | SPMP-11 | dP Control Sensor Flatlined | Warning |  | dP control sensor | dP control sensor | The differential-pressure control sensor shows no change beyond deadband for 4 h while the set is running. A stuck dP sensor drives the whole secondary set open-loop — suppress dependent speed/pressure alerts while this is active.
Pumps (Secondary) | SPMP-12 | Staging Not Responding to Demand | Alert |  | Multi-pump VSD set | speed, dP, dP_sp, pump count | Lead pump at full speed with dP still under target for a sustained period and no additional pump staged in (or the reverse: pumps not shedding at low demand). Staging control not tracking the load.

## How To Use
RCC FDD FAULT TABLES v1.5 — BGIS RCC · part of the controlled set: Standard v1.0 · Register v3.3 · Dashboard · Operator Tool
The central design library: every fault we commit to detecting, with design intent and typical defaults.
It defines WHAT gets detected and gives the designer a starting point; HOW is designed per building.
The Register tracks per-building status; the Operator Tool derives per-asset applicability from this library.
Severity: Critical / Warning / Alert / Info (definitions in the Standard, Section 4).
OOH = also routes to the out-of-hours call-out chain. Routing, not severity.
Lifecycle: Backlog → Built → Configured → Enabled → Validated (+ Blocked / NA). Enabled+Validated = live coverage; Validated = assured.
FDDs satisfied by an existing KODE Event follow the same lifecycle and are marked Validated once confirmed suitable.
COUNTS (live)
Total faults | 180
Critical | 39
Warning | 93
Alert | 44
Info | 4
OOH-routed | 17